## PMS(input)
JCM_ID_F_PMS_ver01.0
JCM Proposed Methodology Spreadsheet Form (input sheet) [Attachment to Proposed Methodology Form]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | QPJh,p | Quantity of heating energy utilized by the project building during the period p |  | GJ/p | Option C | monitored data | Quantity of heating energy utilized by the project building is determined either by (1) a calorimeter or (2) calculation results using a set of different monitored data. In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 is not provided, such monitoring equipment is required to be calibrated. [Approach 1 using a calorimeter] The calorimeter measures the heating value cumulatively for each equipment. [Approach 2 applying calculation results of monitored data] Following formula from the methodology is applied: Where, mPJh,i,t :Quantity of hot water utilized by the equipment i in the project building between time t-1 and time t Th-0,i,t : Outlet temperature of the hot water at time t Th-1,i,t :Inlet temperature of the feed water for hot water at time t mPJh,i,t is measured with a flow meter while Th-0,i,t and Th-1,i,t are measured with thermometers. | [Approach 1] Monitored continuously and recorded at least monthly [Approach 2] Monitored at t interval (at least hourly basis) and recorded at least daily
| (2) | QPJc,p | Quantity of cooling energy utilized by the project building during the period p |  | GJ/p | Option C | monitored data | Quantity of cooling energy utilized by the project building is determined either by (1) a calorimeter or (2) calculation results using a set of different monitored data. 'In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 is not provided, such monitoring equipment is required to calbrate. [Approach 1 using a calorimeter] The calorimeter measures the heating value cumulatively for each equipment. [Approach 2 applying calculation results of monitored data] Following formula from the methodology is applied: Where, mPJc,i,t :Quantity of chilled water utilized by the equipment i in the project building between time t-1 and time t Th-0,i,t : Inlet temperature of the feed water for chilled water at time t Th-1,i,t : Outlet temperature of the chilled water at time t mPJc,i,t is measured with a flow meter while Th-0,i,t and Th-1,i,t are measured with thermometers. | [Approach 1] Monitored continuously and recorded at least monthly [Approach 2] Monitored at t interval (at least hourly basis) and recorded at least daily
| (3) | FCPJ,p | Oil consumed by the project during the period p |  | kL/p | Option B or Option C | Invoice from fuel supplier for Option B or monitored data for Option C | [Option B] Recorded from invoices provided by the fuel supplier. [Option C] Measured with a flow meter, calibrated according to the national regulation. In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 is not provided, such monitoring equipment is required to calbrate. | Recorded Monthly
| (4) | ECHP,m,p | Electricity consumed by the modular HP m operated during the period p |  | MWh/p | Option C | monitored data | 'Measured with an electric meter. In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 is not provided, such monitoring equipment is required to calbrate. Data are recorded at least once a month. | Monitored continuously and recorded monthly
| (5) | ECHP_aux,m,p | Electricity consumed by auxiliary electric equipment for the modular HP m operated during the period p |  | MWh/p | Option C | monitored data | Measured with an electric meter. In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 is not provided, such monitoring equipment is required to calbrate. Data are recorded at least once a month. | Monitored continuously and recorded monthly
| (6) | ECOther,n,p | Electricity consumed by other chilled water generating equipment n operated during the period p |  | MWh/p | Option C | monitored data | Measured with an electric meter. In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 is not provided, such monitoring equipment is required to calbrate. Data are recorded at least once a month. | Monitored continuously and recorded monthly
| (7) | ECOther_aux,n,p | Electricity consumed by auxiliary electric equipment for the other chilled water generating equipment n during the period p |  | MWh/p | Option C | monitored data | Measured with an electric meter. In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 is not provided, such monitoring equipment is required to calbrate. Data are recorded at least once a month. | Monitored continuously and recorded monthly
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| ηREh | Efficiency of the reference equipment for heating energy generation |  | 0.9 | dimensionless | Default value in the methodology (from the CDM methodological tool "Tool to determine the baseline efficiency of thermal or electric energy generation systems", ver.01).
| ηREc | Efficiency of the reference equipment for cooling energy generation |  | 3.7 | dimensionless | Default value in the methodology (from the latest National Standard of Indonesia SNI 6390 available at the time of validation).
| EFREh | CO2 emission factor for the liquid fuel consumed by the reference equipment for heating energy generation |  |  | tCO2/GJ | Either from the publicly available data and/or the latest IPCC default value. [IPCC data] Lower value of the default emission factor is applied in line with the CDM methodological tool “Tool to calculate baseline, project and/or leakage emissions from electricity consumption (Version 01)”.
| Cp | Specific heat capacity of water |  | 4.2 | MJ/tonne- degree Celsius
| ρ | Density of water |  | 1 | tonne/m3
| EFelec | CO2 emission factor for the electricity consumed by the project and the reference equipment When captive power generation is not available at the project site, then the most recent Indonesian national grid emission factor available at the time of validation is applied and fixed for the monitoring period thereafter. When captive power generation is available at the project site, then [EFELEC] is conservatively selected as below and fixed for the monitoring period thereafter: EFELEC = min (EFgrid, EFcaptive) EFcaptive = 0.8 tCO2/MWh* *The most recent emission factor available from CDM approved small scale methodology AMS-I.A at the time of validation is applied. |  | 0.814 | tCO2/MWh | [EFgrid] The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from Updates on Grid Electricity Emission Factors, National Committee on Clean Development Mechanism, Indonesia, unless otherwise instructed by the Joint Committee. [EFcaptive] CDM approved small scale methodology AMS-I.A
| EFfuel | CO2 emission factor for the liquid fuel consumed by the project |  |  | tCO2/kL | Either from the publicly available data and/or the latest IPCC default value. [IPCC data] Lower value of the default emission factor is applied in line with the CDM methodological tool “Tool to calculate baseline, project and/or leakage emissions from electricity consumption (Version 01)”. [Public data] Apply density data from Pertamina website: http://pelumas.pertamina.com/Files/product_all.asp
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 0 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## PMS(calc_process)
JCM_ID_F_PMS_ver01.0
JCM Proposed Methodology Spreadsheet Form (Calculation Process Sheet)
[Attachment to Proposed Methodology Form]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  | N/A | 0 | tCO2/p | ERp
2. Selected default values, etc.
| Efficiency of the reference equipment for heating energy generation |  |  | N/A | 0.9 | - | ηREh
| Efficiency of the reference equipment for cooling energy generation |  |  | N/A | 3.7 | - | ηREc
3. Calculations for reference emissions
| Reference emissions during the period p |  |  | N/A | 0 | tCO2/p | REp
|  | Quantity of heating energy utilized by the project building during the period p |  | N/A | 0 | GJ/y | QPJh,p
|  | Quantity of cooling energy utilized by the project building during the period p |  | N/A | 0 | GJ/y | QPJc,p
|  | Efficiency of the reference equipment for heating energy generation |  | N/A | 0.9 | -- | ηREh
|  | Efficiency of the reference equipment for cooling energy generation |  | N/A | 3.7 | -- | ηREc
|  | CO2 emission factor for the oil consumed by the reference equipment for heating energy generation |  | Oil | 0 | tCO2/GJ | EFREh
|  | CO2 emission factor for the electricity consumed by the project |  | Electricity | 0.814 | tCO2/MWh | EFelec
4. Calculations of the project emissions
| Project emissions during the period p |  |  | N/A | 0 | tCO2/p | PEp
|  | Electricity consumed by the project during the period p |  | Electricity | 0 | MWh/p | ECPJ,p
|  | CO2 emission factor for the electricity consumed by the project |  | N/A | 0.814 | tCO2/MWh | EFelec
|  | Oil consumed by the project during the period p |  | Oil | 0 | kL/p | FCPJ,p
|  | CO2 emission factor for the oil consumed by the project |  | N/A | 0 | tCO2/kL | EFfuel
|  | Electricity consumed by the modular HP m operated during the period p |  | Electricity | 0 | MWh/p | ECHP,m,p
|  | Electricity consumed by auxiliary electric equipment for the modular HP m during the period p |  | Electricity | 0 | MWh/p | ECHP_aux,m,p
|  | Electricity consumed by other chilled water generating equipment n operated during the period p |  | Electricity | 0 | MWh/p | ECOther,n,p
|  | Electricity consumed by auxiliary electric equipment for the other chilled water generating equipment n during the period p |  | Electricity | 0 | MWh/p | ECother_aux,n,p
[List of Default Values]
|  |  | ηREh | 0.9 | -
|  |  | ηREc | 3.7 | -