## Summary Table
Summary
No. | Site Name | Grid Type | Estimated Reference Emissions (tCO2/p) | Estimated Project Emissions (tCO2/p) | Estimated Emission Reduction (tCO2/p) | Estimated Reference Emissions (tCO2/p) | Estimated Project Emissions (tCO2/p) | Estimated Emission Reduction (tCO2/p)
1 | Pulau Putri | Off grid | 43.1315 | 25.929 | 17.2025 | 43.1 | 25.9 | 17
2 | Pulau Pantara | Off grid | 43.1315 | 20.167 | 22.9645 | 43.1 | 20.2 | 22.9
3 | Gunung Kramaian | Off grid | 43.1315 | 34.9077 | 8.2238 | 43.1 | 34.9 | 8.2
4 | Perdau | Off grid | 43.1315 | 29.5015 | 13.63 | 43.1 | 29.5 | 13.6
5 | Matamanis | Off grid | 43.1315 | 21.3338 | 21.7977 | 43.1 | 21.3 | 21.8
6 | Sei Mayang | Off grid | 43.1315 | 26.779 | 16.3525 | 43.1 | 26.8 | 16.3
7 | Muara Lesan | Off grid | 43.1315 | 28.529 | 14.6025 | 43.1 | 28.5 | 14.6
8 | Kota Bangun Empat | Off grid | 43.1315 | 29.5015 | 13.63 | 43.1 | 29.5 | 13.6
9 | Gunung Kuku | Off grid | 43.1315 | 12.3883 | 30.7432 | 43.1 | 12.4 | 30.7
10 | Pulau Galang Baru | Off grid | 43.1315 | 8.4989 | 34.6326 | 43.1 | 8.5 | 34.6
11 | Pantai Pasir Panjang | Off grid | 43.1315 | 11.4937 | 31.6378 | 43.1 | 11.5 | 31.6
12 | Galang Baru Tengah | Off grid | 43.1315 | 8.8879 | 34.2436 | 43.1 | 8.9 | 34.2
13 | Sungsang | Off grid | 43.1315 | 23.2785 | 19.8531 | 43.1 | 23.3 | 19.8
14 | Karanganyar2 | Poor grid | 32.8037 | 30.1931 | 2.6107 | 32.8 | 30.2 | 2.6
15 | Bukit Barapung | Off grid | 43.1315 | 17.3667 | 25.7649 | 43.1 | 17.4 | 25.7
16 | HUT Tanah Merah | Off grid | 43.1315 | 28.4903 | 14.6412 | 43.1 | 28.5 | 14.6
17 | Tirta Agung Mangsang | Off grid | 43.1315 | 12.466 | 30.6655 | 43.1 | 12.5 | 30.6
18 | Gunung Sari Kampar | Poor grid | 22.5437 | 18.2063 | 4.3374 | 22.5 | 18.2 | 4.3
19 | Kulim2 | Poor grid | 37.7563 | 35.5232 | 2.2332 | 37.8 | 35.5 | 2.3
20 | Sukamakmur Kampar Kiri | Poor grid | 22.7044 | 18.1208 | 4.5836 | 22.7 | 18.1 | 4.6
|  | Total |  |  | 364.3504 | 805.4 | 441.6 | 363.6

## MPS(input)_1.Pulau Putri
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p | 0 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p | 33.215 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p | 0.4745 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p | 0 | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (5) | Ti,p | Total hours of operation of BTSi during the period p | 8760 | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored daily and recorded monthly | n/a
| (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p | 10585 | L/p | Option C | monitored data | Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Recorded at every filling time | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid | Grid CO2 emission factor |  | 0.903 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 17 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)_1.Pulau Putri
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | 17.2025 | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | 43.1315 | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 33.6895 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 0 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 33.215 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0.4745 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 0 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 8760 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.903 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 25.929 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 0 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.903 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 10585 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ

## MSS_1.Pulau Putri
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for final check of monitoring results and project implemetation
| Data Monitoring Manager | Responsible for preparing monitoring report, approving the recorded data and archived data, and training of monitoring personnel.
| System Implementation Manager (based in Japan) | Responsible for installation of monitiroing equipment, data collection and storage procedure, calibrations.
| Facility Manager and Engineer (based in Jakarta, Indonesia) | Responsible for collecting and compiling monitored data (except diesel consumption) to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to System Implementation Manager.
| BTS owner, and Manager (based in Jakarta, Indonesia) | Responsible for BTS facility, and for collecting, recording and compiling diesel consumption data to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to Facility Manager.

## MPS(input)_2.Pulau Pantara
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p | 0 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p | 25.7 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p | 0.50212 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p | 0 | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (5) | Ti,p | Total hours of operation of BTSi during the period p | 8760 | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored daily and recorded monthly | n/a
| (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p | 8232.8 | L/p | Option C | monitored data | Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Recorded at every filling time | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid | Grid CO2 emission factor |  | 0.903 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 22 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)_2.Pulau Panta
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | 22.9645 | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | 43.1315 | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 26.2021 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 0 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 25.7 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0.50212 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 0 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 8760 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.903 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 20.167 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 0 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.903 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 8232.8 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ

## MSS _2.Pulau Pantara
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for final check of monitoring results and project implemetation
| Data Monitoring Manager | Responsible for preparing monitoring report, approving the recorded data and archived data, and training of monitoring personnel.
| System Implementation Manager (based in Japan) | Responsible for installation of monitiroing equipment, data collection and storage procedure, calibrations.
| Facility Manager and Engineer (based in Jakarta, Indonesia) | Responsible for collecting and compiling monitored data (except diesel consumption) to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to System Implementation Manager.
| BTS owner, and Manager (based in Jakarta, Indonesia) | Responsible for BTS facility, and for collecting, recording and compiling diesel consumption data to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to Facility Manager.

## MPS(input)_3.Gunung Kramaian
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p | 0 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p | 44.4 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p | 0.6276 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p | 0 | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (5) | Ti,p | Total hours of operation of BTSi during the period p | 8760 | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored daily and recorded monthly | n/a
| (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p | 14250.4 | L/p | Option C | monitored data | Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Recorded at every filling time | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid | Grid CO2 emission factor |  | 1.512 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 8 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)_3.Gunung Kram
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | 8.2238 | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | 43.1315 | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 45.0276 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 0 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 44.4 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0.6276 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 0 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 8760 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 1.512 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 34.9077 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 0 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 1.512 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 14250.4 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ

## MSS_3.Gunung Kram
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for final check of monitoring results and project implemetation
| Data Monitoring Manager | Responsible for preparing monitoring report, approving the recorded data and archived data, and training of monitoring personnel.
| System Implementation Manager (based in Japan) | Responsible for installation of monitiroing equipment, data collection and storage procedure, calibrations.
| Facility Manager and Engineer (based in Jakarta, Indonesia) | Responsible for collecting and compiling monitored data (except diesel consumption) to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to System Implementation Manager.
| BTS owner, and Manager (based in Jakarta, Indonesia) | Responsible for BTS facility, and for collecting, recording and compiling diesel consumption data to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to Facility Manager.

## MPS(input)_4.Perdau
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p | 0 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p | 37.5 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p | 0.6276 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p | 0 | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (5) | Ti,p | Total hours of operation of BTSi during the period p | 8760 | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored daily and recorded monthly | n/a
| (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p | 12043.4 | L/p | Option C | monitored data | Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Recorded at every filling time | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid | Grid CO2 emission factor |  | 0.76 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 13 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)_4.Perdau
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | 13.63 | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | 43.1315 | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 38.1276 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 0 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 37.5 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0.6276 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 0 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 8760 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.76 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 29.5015 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 0 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.76 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 12043.4 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ

## MSS_4.Perdau
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for final check of monitoring results and project implemetation
| Data Monitoring Manager | Responsible for preparing monitoring report, approving the recorded data and archived data, and training of monitoring personnel.
| System Implementation Manager (based in Japan) | Responsible for installation of monitiroing equipment, data collection and storage procedure, calibrations.
| Facility Manager and Engineer (based in Jakarta, Indonesia) | Responsible for collecting and compiling monitored data (except diesel consumption) to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to System Implementation Manager.
| BTS owner, and Manager (based in Jakarta, Indonesia) | Responsible for BTS facility, and for collecting, recording and compiling diesel consumption data to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to Facility Manager.

## MPS(input)_5.Matamanis
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p | 0 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p | 27.2 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p | 0.5021 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p | 0 | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (5) | Ti,p | Total hours of operation of BTSi during the period p | 8760 | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored daily and recorded monthly | n/a
| (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p | 8709.1 | L/p | Option C | monitored data | Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Recorded at every filling time | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid | Grid CO2 emission factor |  | 0.76 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 21 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)_5.Matamanis
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | 21.7977 | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | 43.1315 | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 27.7021 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 0 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 27.2 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0.5021 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 0 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 8760 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.76 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 21.3338 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 0 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.76 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 8709.1 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ

## MSS_5.Matamanis
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for final check of monitoring results and project implemetation
| Data Monitoring Manager | Responsible for preparing monitoring report, approving the recorded data and archived data, and training of monitoring personnel.
| System Implementation Manager (based in Japan) | Responsible for installation of monitiroing equipment, data collection and storage procedure, calibrations.
| Facility Manager and Engineer (based in Jakarta, Indonesia) | Responsible for collecting and compiling monitored data (except diesel consumption) to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to System Implementation Manager.
| BTS owner, and Manager (based in Jakarta, Indonesia) | Responsible for BTS facility, and for collecting, recording and compiling diesel consumption data to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to Facility Manager.

## MPS(input)_6.Sei Mayang
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p | 0 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p | 34.1 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p | 0.5021 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p | 0 | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (5) | Ti,p | Total hours of operation of BTSi during the period p | 8760 | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored daily and recorded monthly | n/a
| (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p | 10932 | L/p | Option C | monitored data | Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Recorded at every filling time | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid | Grid CO2 emission factor |  | 0.76 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 16 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)_6.Sei Mayang
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | 16.3525 | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | 43.1315 | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 34.6021 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 0 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 34.1 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0.5021 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 0 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 8760 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.76 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 26.779 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 0 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.76 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 10932 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ

## MSS_6.Sei Mayang
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for final check of monitoring results and project implemetation
| Data Monitoring Manager | Responsible for preparing monitoring report, approving the recorded data and archived data, and training of monitoring personnel.
| System Implementation Manager (based in Japan) | Responsible for installation of monitiroing equipment, data collection and storage procedure, calibrations.
| Facility Manager and Engineer (based in Jakarta, Indonesia) | Responsible for collecting and compiling monitored data (except diesel consumption) to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to System Implementation Manager.
| BTS owner, and Manager (based in Jakarta, Indonesia) | Responsible for BTS facility, and for collecting, recording and compiling diesel consumption data to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to Facility Manager.

## MPS(input)_7.Muara Lesan
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p | 0 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p | 36.3 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p | 0.5021 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p | 0 | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (5) | Ti,p | Total hours of operation of BTSi during the period p | 8760 | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored daily and recorded monthly | n/a
| (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p | 11646.4 | L/p | Option C | monitored data | Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Recorded at every filling time | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid | Grid CO2 emission factor |  | 0.76 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 14 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)_7.Muara Lesan
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | 14.6025 | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | 43.1315 | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 36.8021 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 0 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 36.3 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0.5021 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 0 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 8760 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.76 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 28.529 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 0 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.76 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 11646.4 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ

## MSS_7.Muara Lesan
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for final check of monitoring results and project implemetation
| Data Monitoring Manager | Responsible for preparing monitoring report, approving the recorded data and archived data, and training of monitoring personnel.
| System Implementation Manager (based in Japan) | Responsible for installation of monitiroing equipment, data collection and storage procedure, calibrations.
| Facility Manager and Engineer (based in Jakarta, Indonesia) | Responsible for collecting and compiling monitored data (except diesel consumption) to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to System Implementation Manager.
| BTS owner, and Manager (based in Jakarta, Indonesia) | Responsible for BTS facility, and for collecting, recording and compiling diesel consumption data to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to Facility Manager.

## MPS(input)_8.Kota Bangun Empat
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p | 0 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p | 37.5 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p | 0.6276 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p | 0 | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (5) | Ti,p | Total hours of operation of BTSi during the period p | 8760 | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored daily and recorded monthly | n/a
| (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p | 12043.4 | L/p | Option C | monitored data | Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Recorded at every filling time | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid | Grid CO2 emission factor |  | 0.76 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 13 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)_8.Kota Bangun
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | 13.63 | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | 43.1315 | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 38.1276 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 0 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 37.5 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0.6276 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 0 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 8760 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.76 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 29.5015 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 0 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.76 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 12043.4 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ

## MSS_8.Kota Bangun Empat
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for final check of monitoring results and project implemetation
| Data Monitoring Manager | Responsible for preparing monitoring report, approving the recorded data and archived data, and training of monitoring personnel.
| System Implementation Manager (based in Japan) | Responsible for installation of monitiroing equipment, data collection and storage procedure, calibrations.
| Facility Manager and Engineer (based in Jakarta, Indonesia) | Responsible for collecting and compiling monitored data (except diesel consumption) to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to System Implementation Manager.
| BTS owner, and Manager (based in Jakarta, Indonesia) | Responsible for BTS facility, and for collecting, recording and compiling diesel consumption data to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to Facility Manager.

## MPS(input)_9.Gunung Kuku
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p | 0 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p | 15.8 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p | 0.2511 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p | 0 | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (5) | Ti,p | Total hours of operation of BTSi during the period p | 8760 | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored daily and recorded monthly | n/a
| (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p | 5057.3 | L/p | Option C | monitored data | Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Recorded at every filling time | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid | Grid CO2 emission factor |  | 0.76 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 30 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)_9.Gunung Kuku
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | 30.7432 | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | 43.1315 | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 16.0511 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 0 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 15.8 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0.2511 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 0 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 8760 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.76 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 12.3883 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 0 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.76 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 5057.3 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ

## MSS_9.Gunung Kuku
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for final check of monitoring results and project implemetation
| Data Monitoring Manager | Responsible for preparing monitoring report, approving the recorded data and archived data, and training of monitoring personnel.
| System Implementation Manager (based in Japan) | Responsible for installation of monitiroing equipment, data collection and storage procedure, calibrations.
| Facility Manager and Engineer (based in Jakarta, Indonesia) | Responsible for collecting and compiling monitored data (except diesel consumption) to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to System Implementation Manager.
| BTS owner, and Manager (based in Jakarta, Indonesia) | Responsible for BTS facility, and for collecting, recording and compiling diesel consumption data to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to Facility Manager.

## MPS(input)_10.Pulau Galang Baru
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p | 0 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p | 10.8 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p | 0.2511 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p | 0 | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (5) | Ti,p | Total hours of operation of BTSi during the period p | 8760 | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored daily and recorded monthly | n/a
| (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p | 3469.5 | L/p | Option C | monitored data | Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Recorded at every filling time | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid | Grid CO2 emission factor |  | 0.953 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 34 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)_10.Pulau Gala
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | 34.6326 | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | 43.1315 | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 11.0511 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 0 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 10.8 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0.2511 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 0 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 8760 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.953 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 8.4989 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 0 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.953 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 3469.5 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ

## MSS_10.Pulau Galang Baru
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for final check of monitoring results and project implemetation
| Data Monitoring Manager | Responsible for preparing monitoring report, approving the recorded data and archived data, and training of monitoring personnel.
| System Implementation Manager (based in Japan) | Responsible for installation of monitiroing equipment, data collection and storage procedure, calibrations.
| Facility Manager and Engineer (based in Jakarta, Indonesia) | Responsible for collecting and compiling monitored data (except diesel consumption) to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to System Implementation Manager.
| BTS owner, and Manager (based in Jakarta, Indonesia) | Responsible for BTS facility, and for collecting, recording and compiling diesel consumption data to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to Facility Manager.

## MPS(input)_11.Pantai Pasir Panj
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p | 0 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p | 14.6282 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p | 0.2511 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p | 0 | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (5) | Ti,p | Total hours of operation of BTSi during the period p | 8760 | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored daily and recorded monthly | n/a
| (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p | 4692.0953 | L/p | Option C | monitored data | Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Recorded at every filling time | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid | Grid CO2 emission factor |  | 0.953 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 31 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)_11. Pantai Pa
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | 31.6378 | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | 43.1315 | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 14.8793 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 0 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 14.6282 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0.2511 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 0 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 8760 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.953 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 11.4937 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 0 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.953 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 4692.0953 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ

## MSS_11.Pantai Pasir Panj
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for final check of monitoring results and project implemetation
| Data Monitoring Manager | Responsible for preparing monitoring report, approving the recorded data and archived data, and training of monitoring personnel.
| System Implementation Manager (based in Japan) | Responsible for installation of monitiroing equipment, data collection and storage procedure, calibrations.
| Facility Manager and Engineer (based in Jakarta, Indonesia) | Responsible for collecting and compiling monitored data (except diesel consumption) to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to System Implementation Manager.
| BTS owner, and Manager (based in Jakarta, Indonesia) | Responsible for BTS facility, and for collecting, recording and compiling diesel consumption data to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to Facility Manager.

## MPS(input)_12.Galang Baru Tenga
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p | 0 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p | 11.3 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p | 0.2511 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p | 0 | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (5) | Ti,p | Total hours of operation of BTSi during the period p | 8760 | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored daily and recorded monthly | n/a
| (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p | 3628.3 | L/p | Option C | monitored data | Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Recorded at every filling time | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid | Grid CO2 emission factor |  | 0.953 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 34 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)_12.Galang Bar
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | 34.2436 | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | 43.1315 | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 11.5511 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 0 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 11.3 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0.2511 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 0 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 8760 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.953 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 8.8879 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 0 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.953 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 3628.3 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ

## MSS_12.Galang Baru Tengah
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for final check of monitoring results and project implemetation
| Data Monitoring Manager | Responsible for preparing monitoring report, approving the recorded data and archived data, and training of monitoring personnel.
| System Implementation Manager (based in Japan) | Responsible for installation of monitiroing equipment, data collection and storage procedure, calibrations.
| Facility Manager and Engineer (based in Jakarta, Indonesia) | Responsible for collecting and compiling monitored data (except diesel consumption) to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to System Implementation Manager.
| BTS owner, and Manager (based in Jakarta, Indonesia) | Responsible for BTS facility, and for collecting, recording and compiling diesel consumption data to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to Facility Manager.

## MPS(input)_13.Sungsang
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p | 0 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p | 29.6267 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p | 0.5021 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p | 0 | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (5) | Ti,p | Total hours of operation of BTSi during the period p | 8760 | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored daily and recorded monthly | n/a
| (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p | 9502.9778 | L/p | Option C | monitored data | Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Recorded at every filling time | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid | Grid CO2 emission factor |  | 0.855 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 19 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)_13.Sungsang
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | 19.8531 | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | 43.1315 | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 30.1288 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 0 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 29.6267 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0.5021 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 0 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 8760 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.855 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 23.2785 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 0 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.855 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 9502.9778 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ

## MSS_13.Sungsang
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for final check of monitoring results and project implemetation
| Data Monitoring Manager | Responsible for preparing monitoring report, approving the recorded data and archived data, and training of monitoring personnel.
| System Implementation Manager (based in Japan) | Responsible for installation of monitiroing equipment, data collection and storage procedure, calibrations.
| Facility Manager and Engineer (based in Jakarta, Indonesia) | Responsible for collecting and compiling monitored data (except diesel consumption) to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to System Implementation Manager.
| BTS owner, and Manager (based in Jakarta, Indonesia) | Responsible for BTS facility, and for collecting, recording and compiling diesel consumption data to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to Facility Manager.

## MPS(input)_14.Karanganyar2
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p | 30.7 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p | 5 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p | 0.2511 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p | 7300 | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (5) | Ti,p | Total hours of operation of BTSi during the period p | 8760 | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored daily and recorded monthly | n/a
| (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p | 1610.3 | L/p | Option C | monitored data | Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Recorded at every filling time | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid | Grid CO2 emission factor |  | 0.855 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 2 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)_14.Karanganya
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | 2.6107 | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | 32.8037 | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 35.9511 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 30.7 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 5 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0.2511 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 7300 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 8760 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.855 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 30.1931 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 30.7 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.855 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 1610.3 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ

## MSS_14.Karanganyar2
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for final check of monitoring results and project implemetation
| Data Monitoring Manager | Responsible for preparing monitoring report, approving the recorded data and archived data, and training of monitoring personnel.
| System Implementation Manager (based in Japan) | Responsible for installation of monitiroing equipment, data collection and storage procedure, calibrations.
| Facility Manager and Engineer (based in Jakarta, Indonesia) | Responsible for collecting and compiling monitored data (except diesel consumption) to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to System Implementation Manager.
| BTS owner, and Manager (based in Jakarta, Indonesia) | Responsible for BTS facility, and for collecting, recording and compiling diesel consumption data to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to Facility Manager.

## MPS(input)_15.Bukit Barapung
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p | 0 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p | 22.0779 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p | 0.5021 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p | 0 | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (5) | Ti,p | Total hours of operation of BTSi during the period p | 8760 | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored daily and recorded monthly | n/a
| (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p | 7089.6 | L/p | Option C | monitored data | Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Recorded at every filling time | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid | Grid CO2 emission factor |  | 0.855 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 25 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)_15.Bukit Bara
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | 25.7649 | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | 43.1315 | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 22.58 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 0 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 22.0779 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0.5021 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 0 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 8760 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.855 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 17.3667 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 0 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.855 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 7089.6 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ

## MSS_15.Bukit Barapung
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for final check of monitoring results and project implemetation
| Data Monitoring Manager | Responsible for preparing monitoring report, approving the recorded data and archived data, and training of monitoring personnel.
| System Implementation Manager (based in Japan) | Responsible for installation of monitiroing equipment, data collection and storage procedure, calibrations.
| Facility Manager and Engineer (based in Jakarta, Indonesia) | Responsible for collecting and compiling monitored data (except diesel consumption) to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to System Implementation Manager.
| BTS owner, and Manager (based in Jakarta, Indonesia) | Responsible for BTS facility, and for collecting, recording and compiling diesel consumption data to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to Facility Manager.

## MPS(input)_16.HUT Tanah Merah
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p | 0 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p | 36.3 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p | 0.6276 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p | 0 | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (5) | Ti,p | Total hours of operation of BTSi during the period p | 8760 | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored daily and recorded monthly | n/a
| (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p | 11630.6 | L/p | Option C | monitored data | Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Recorded at every filling time | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid | Grid CO2 emission factor |  | 0.855 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 14 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)_16.HUT Tanah
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | 14.6412 | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | 43.1315 | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 36.9276 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 0 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 36.3 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0.6276 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 0 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 8760 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.855 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 28.4903 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 0 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.855 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 11630.6 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ

## MSS_16.HUT Tanah Merah
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for final check of monitoring results and project implemetation
| Data Monitoring Manager | Responsible for preparing monitoring report, approving the recorded data and archived data, and training of monitoring personnel.
| System Implementation Manager (based in Japan) | Responsible for installation of monitiroing equipment, data collection and storage procedure, calibrations.
| Facility Manager and Engineer (based in Jakarta, Indonesia) | Responsible for collecting and compiling monitored data (except diesel consumption) to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to System Implementation Manager.
| BTS owner, and Manager (based in Jakarta, Indonesia) | Responsible for BTS facility, and for collecting, recording and compiling diesel consumption data to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to Facility Manager.

## MPS(input)_17.Tirta Agung Mangs
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p | 0 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p | 15.8954 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p | 0.2511 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p | 0 | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (5) | Ti,p | Total hours of operation of BTSi during the period p | 8760 | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored daily and recorded monthly | n/a
| (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p | 5089 | L/p | Option C | monitored data | Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Recorded at every filling time | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid | Grid CO2 emission factor |  | 0.855 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 30 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)_17.Tirta Agun
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | 30.6655 | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | 43.1315 | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 16.1465 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 0 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 15.8954 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0.2511 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 0 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 8760 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.855 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 12.466 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 0 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.855 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 5089 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ

## MSS_17.Tirta Agung Mangsang
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for final check of monitoring results and project implemetation
| Data Monitoring Manager | Responsible for preparing monitoring report, approving the recorded data and archived data, and training of monitoring personnel.
| System Implementation Manager (based in Japan) | Responsible for installation of monitiroing equipment, data collection and storage procedure, calibrations.
| Facility Manager and Engineer (based in Jakarta, Indonesia) | Responsible for collecting and compiling monitored data (except diesel consumption) to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to System Implementation Manager.
| BTS owner, and Manager (based in Jakarta, Indonesia) | Responsible for BTS facility, and for collecting, recording and compiling diesel consumption data to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to Facility Manager.

## MPS(input)_18.Gunung Sari Kampa
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p | 18.5 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p | 2.8 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p | 0.2511 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p | 7300 | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (5) | Ti,p | Total hours of operation of BTSi during the period p | 8760 | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored daily and recorded monthly | n/a
| (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p | 975.2 | L/p | Option C | monitored data | Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Recorded at every filling time | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid | Grid CO2 emission factor |  | 0.855 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 4 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)_18.Gunung Sar
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | 4.3374 | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | 22.5437 | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 21.5511 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 18.5 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 2.8 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0.2511 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 7300 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 8760 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.855 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 18.2063 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 18.5 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.855 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 975.2 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ

## MSS_18.Gunung Sari Kampa
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for final check of monitoring results and project implemetation
| Data Monitoring Manager | Responsible for preparing monitoring report, approving the recorded data and archived data, and training of monitoring personnel.
| System Implementation Manager (based in Japan) | Responsible for installation of monitiroing equipment, data collection and storage procedure, calibrations.
| Facility Manager and Engineer (based in Jakarta, Indonesia) | Responsible for collecting and compiling monitored data (except diesel consumption) to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to System Implementation Manager.
| BTS owner, and Manager (based in Jakarta, Indonesia) | Responsible for BTS facility, and for collecting, recording and compiling diesel consumption data to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to Facility Manager.

## MPS(input)_19.Kulim2
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p | 36.1 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p | 6.3 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p | 0.5021 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p | 7300 | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (5) | Ti,p | Total hours of operation of BTSi during the period p | 8760 | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored daily and recorded monthly | n/a
| (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p | 1901.4 | L/p | Option C | monitored data | Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Recorded at every filling time | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid | Grid CO2 emission factor |  | 0.855 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 2 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)_19.Kulim2
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | 2.2332 | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | 37.7563 | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 42.9021 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 36.1 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 6.3 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0.5021 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 7300 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 8760 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.855 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 35.5232 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 36.1 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.855 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 1901.4 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ

## MSS_19.Kulim2
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for final check of monitoring results and project implemetation
| Data Monitoring Manager | Responsible for preparing monitoring report, approving the recorded data and archived data, and training of monitoring personnel.
| System Implementation Manager (based in Japan) | Responsible for installation of monitiroing equipment, data collection and storage procedure, calibrations.
| Facility Manager and Engineer (based in Jakarta, Indonesia) | Responsible for collecting and compiling monitored data (except diesel consumption) to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to System Implementation Manager.
| BTS owner, and Manager (based in Jakarta, Indonesia) | Responsible for BTS facility, and for collecting, recording and compiling diesel consumption data to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to Facility Manager.

## MPS(input)_20.Sukamakmur Kampar
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p | 18.4 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p | 3 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p | 0.3766 | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The manufacturer's specification for the measuring equipment has been prepared by the time of installation. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p | 7300 | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored continuously and recorded monthly | n/a
| (5) | Ti,p | Total hours of operation of BTSi during the period p | 8760 | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Monitored daily and recorded monthly | n/a
| (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p | 975.2 | L/p | Option C | monitored data | Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. The data monitored is kept and archived electronically for two years after the final issuance of credits. | Recorded at every filling time | n/a
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid | Grid CO2 emission factor |  | 0.855 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 4 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)_20.Sukamakmur
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | 4.5836 | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | 22.7044 | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 21.7766 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 18.4 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 3 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0.3766 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 7300 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 8760 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.855 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 18.1208 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 18.4 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.855 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 975.2 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ

## MSS_20.Sukamakmur Kampar Kiri
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for final check of monitoring results and project implemetation
| Data Monitoring Manager | Responsible for preparing monitoring report, approving the recorded data and archived data, and training of monitoring personnel.
| System Implementation Manager (based in Japan) | Responsible for installation of monitiroing equipment, data collection and storage procedure, calibrations.
| Facility Manager and Engineer (based in Jakarta, Indonesia) | Responsible for collecting and compiling monitored data (except diesel consumption) to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to System Implementation Manager.
| BTS owner, and Manager (based in Jakarta, Indonesia) | Responsible for BTS facility, and for collecting, recording and compiling diesel consumption data to be reported to Data Monitoring Manager and checking any defect of installed equipment, including monitoring equipment to be reported to Facility Manager.

## MRS(input)
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Report Sheet (Input Sheet) [For Verification]
Table 1: Parameters monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k)
| Monitoring period | Monitoring point No. | Parameters | Description of data | Monitored Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
|  | (1) | ECi,grid,p | The amount of grid electricity consumed at BTSi during the period p |  | MWh/p | Option C | monitored data | Measuring equipment is installed to measure grid electricity consumption at project BTSi. The measuring equipment is replaced or calibrated at an interval following the regulations in the country in which the measuring equipment is commonly used or according to the manufacturer's recommendation, unless a type approval, manufacturer's specification, or certification issued by an entity accredited under international/national standards for the measuring equipment has been prepared by the time of installation. | Monitored continuously and recorded monthly | n/a
|  | (2) | ECi,diesel,p | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by the project diesel generator at project BTSi. The measuring equipment is replaced or calibrated at an interval following the regulations in the country in which the measuring equipment is commonly used or according to the manufacturer's recommendation, unless a type approval, manufacturer's specification, or certification issued by an entity accredited under international/national standards for the measuring equipment has been prepared by the time of installation. | Monitored continuously and recorded monthly | n/a
|  | (3) | ECi,solar,p | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | MWh/p | Option C | monitored data | Measuring equipment is installed to measure electricity generated by solar PV system at project BTSi. The measuring equipment is replaced or calibrated at an interval following the regulations in the country in which the measuring equipment is commonly used or according to the manufacturer's recommendation, unless a type approval, manufacturer's specification, or certification issued by an entity accredited under international/national standards for the measuring equipment has been prepared by the time of installation. | Monitored continuously and recorded monthly | n/a
|  | (4) | τi,p | Hours for which electricity is available from grid at BTSi during the period p |  | h/p | Option C | monitored data | Sensor logger is installed to measure hours for which of electricity is available from grid. The sensor is replaced or calibrated at an interval following the regulations in the country in which the sensor is commonly used or according to the manufacturer's recommendation, unless a type approval, manufacturer's specification, or certification issued by an entity accredited under international/national standards for the sensor has been prepared by the time of installation. | Monitored continuously and recorded monthly | n/a
|  | (5) | Ti,p | Total hours of operation of BTSi during the period p |  | h/p | Option C | monitored data | Total hours of operation of BTSi is determined based on the following calculation result: Ti,p = Di,p * 24 Where, Di,p = Days of operation of BTSi during the period p Di,p is counted as the actual number of days between starting date (DD/MM/YYYY) and end date (DD/MM/YYYY) of the monitoring period. If there are days on which BTSi is not operating, the number of days should be subtracted from the total number of days monitored. | Monitored daily and recorded monthly | n/a
|  | (6) | FCi,diesel,p | The quantity of diesel consumed at BTSi during the period p |  | L/p | Option C | monitored data | [Option A] Diesel consumption is determined by recording the quantity of the filled fuel which is refilled to fill up the tank at the project BTSi. [Option B] Measured with a flow meter, calibrated according to the national regulation. For option B, flow meter is replaced or calibrated at an interval following the regulation in the country in which the flow meter is commonly used or according to the manufacturer's recommendation, unless a type approval, manufacturer's specification, or certification issued by an entity accredited under international/national standards for the flow meter has been prepared by the time of installation. | [Option A] Recorded monthly [Option B] Monitored continuously and recorded monthly | n/a
Table 2: Project-specific parameters fixed ex ante
| (a) |  | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters |  | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| φi |  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  | 2.01 | L/h | Specification of generator. Manufacturer’s data. If more than one diesel generators are equipped at the project BTS, the most efficient value among the design efficiency of the equipped diesel generators is adopted for the calculation of the reference emissions. |  |  | n/a
| EFgrid |  | Grid CO2 emission factor |  | 0.903 | tCO2/MWh | The most recent value available at the time of validation is applied and fixed for the monitoring period thereafter. The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism Indonesian DNA for CDM unless otherwise instructed by the Joint Committee. |  |  | n/a
| ρdiesel |  | Weighted average density of diesel |  | 0.815 | kg/L | a) Values provided by the fuel supplier in invoices, or b) Regional or national default value. |  |  | n/a
| NCVdiesel |  | Net calorific value of diesel |  | 41.4 | TJ/Gg | IPCC default values provided in table 1.2 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
| EFdiesel |  | Diesel CO2 emission factor |  | 72600 | kgCO2/TJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | n/a
Table3: Ex-post calculation of CO2 emission reductions
| Monitoring Period |  | CO2 emission reductions |  | Units
|  |  | #DIV/0! |  | tCO2/p
[Monitoring option]
| Option A |  | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B |  | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C |  | Based on the actual measurement using measuring equipments (Data used: measured values)

## MRS(calc_process)
Monitoring Spreadsheet: JCM_ID_AM014_ver01.0
Reference Number: ID016
Monitoring Report Sheet (Calculation Process Sheet) [For Verification]
1. Calculations for emission reductions |  |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  |  | n/a | #DIV/0! | tCO2/p | ERp
2. Selected default values, etc.
| Net calorific value of diesel |  |  |  | Diesel | 41.4 | TJ/Gg | NCVdiesel
| Diesel CO2 emission factor |  |  |  | Diesel | 72600 | kgCO2/TJ | EFdiesel
3. Calculations for reference emissions
| Reference emissions during the period p |  |  |  | n/a | #DIV/0! | tCO2/p | REp
|  | Total electricity consumption at BTSi during the period p |  |  | Electricity | 0 | MWh/p | ECi,p
|  |  | The amount of grid electricity consumed at BTSi during the period p |  | Electricity | 0 | MWh/p | ECi,grid,p
|  |  | The amount of electricity generated by the project diesel generator at BTSi during the period p |  | Electricity | 0 | MWh/p | ECi,diesel,p
|  |  | The amount of electricity generated by the project solar PV system at BTSi during the period p |  | Electricity | 0 | MWh/p | ECi,solar,p
|  | Hours for which electricity is available from grid at BTSi during the period p |  |  | n/a | 0 | h/p | τi,p
|  | Total hours of operation of BTSi during the period p |  |  | n/a | 0 | h/p | Ti,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.903 | tCO2/MWh | EFgrid
|  | Design efficiency of diesel generator operated at the project BTS at the time of validation at 25% load to be installed at BTSi |  |  | n/a | 2.01 | L/h | φi
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
4. Calculations of the project emissions
| Project emissions during the period p |  |  |  | n/a | 0 | tCO2/p | PEp
|  | The amount of grid electricity consumed at BTSi during the period p |  |  | Electricity | 0 | MWh/p | ECi,grid,p
|  | Grid CO2 emission factor |  |  | Electricity | 0.903 | tCO2/MWh | EFgrid
|  | The quantity of diesel consumed at BTSi during the period p |  |  | Diesel | 0 | L/p | FCi,diesel,p
|  | Weighted average density of diesel |  |  | Diesel | 0.815 | kg/L | ρdiesel
[List of Default Values]
|  |  |  | Net calorific value of diesel | 41.4 | TJ/Gg
|  |  |  | Diesel CO2 emission factor | 72600 | kgCO2/TJ