## MPS(input)
Monitoring Spreadsheet: JCM_ID_AM015_ver01.0
Reference Number: ID022
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | FCp,i,j,PJ | The amount of fuel consumption of project boiler i using the fuel type j (=natural gas or LPG) during the period p | 800000 | Nm3/p or t/p | Option C | Measured data | [For Option B] Data is collected and recorded from the invoices by the fuel supply company. [For Option C] Data is measured by measuring equipments in the factory. - Specification of measuring equipments: 1) Fuel flow meter is applied for measurement of fuel consumption of the project boilers. 2) Meter is certified in compliance with national / regional / international standards on fuel flow meter. - Measuring and recording: 1) Measured data is automatically sent to a server where data is recorded and stored by measuring equipments with manufacture's specification within ±5% accuracy level which is required as the instrument error in Joint Crediting Mechanism Guidelines for Developing Project Design Document and Monitoring Report. 2) Recorded and compiled data is checked its integrity once a month with monitoring manual by responsible staff. - Calibration: The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of installation. | Continuously | For natural gas or LPG
| (2) | FCp,i,j,PJ | The amount of fuel consumption of project boiler i using the fuel type j (=diesel oil) during the period p | 0 | t/p | Option B or Option C | Invoice from fuel supply company or measured data | [For Option B] Data is collected and recorded from the invoices by the fuel supply company. [For Option C] Data is measured by measuring equipments in the factory. - Specification of measuring equipments: 1) Fuel flow meter is applied for measurement of fuel consumption of the project boilers. 2) Meter is certified in compliance with national / regional / international standards on fuel flow meter. - Measuring and recording: 1) Measured data is automatically sent to a server where data is recorded and stored. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of installation. | Continuously | For diesel oil
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| NCVi,j,PJ | Net calorific value of fuel used by the project boiler i for the fuel type j |  | 0.0331 | GJ/Nm3 or GJ/t | (1) Net calorific value (lower heating value) provided by fuel supplier or boiler manufacturer, (2) IPCC default values at the lower limit in Table 1.2 of Chapter 1 of Vol. 2 of the “2006 IPCC Guidelines on National GHG Inventories” (when (1) is not available, apply (2)) |  |  | For natural gas or LPG
| NCVi,j,PJ | Net calorific value of fuel used by the project boiler i for the fuel type j |  |  | GJ/t | (1) Net calorific value (lower heating value) provided by fuel supplier or boiler manufacturer, (2) IPCC default values at the lower limit in Table 1.2 of Chapter 1 of Vol. 2 of the “2006 IPCC Guidelines on National GHG Inventories” (when (1) is not available, apply (2)) |  |  | For diesel oil
| EFi,j,PJ | CO2 emission factor of fuel used by the project boiler i for the fuel type j |  | 0.0543 | tCO2/GJ | IPCC default values in Table 1.4 of Chapter 1 of Vol. 2 of the “2006 IPCC Guidelines on National GHG Inventories" |  |  | For natural gas or LPG
| EFi,j,PJ | CO2 emission factor of fuel used by the project boiler i for the fuel type j |  |  | tCO2/GJ | IPCC default values in Table 1.4 of Chapter 1 of Vol. 2 of the “2006 IPCC Guidelines on National GHG Inventories" |  |  | For diesel oil
| EFRE | CO2 emission factor of fuel used by reference boiler |  | 0.0543 | tCO2/GJ | IPCC default values at the lower limit in Table 1.4 of Chapter 1 of Vol. 2 of the “2006 IPCC Guidelines on National GHG Inventories" In case the project boiler replaces the existing boiler or the planned boiler whose plan is once approved officially such as with boiler installation permit or environmental impact assessment, CO2 emission factor of the fuel used by the existing or planned boiler is applied. Otherwise, the value of the fuel used by the project boiler i is applied.
| ηi,PJ | Efficiency of project boiler i |  | 0.95 | - | Specifications of the project boiler or factory test data of the project boiler by the manufacturer
| ηRE | Efficiency of reference boiler |  | 0.89 | - | The default value set in the methodologies
| BFi,PJ | Blow flow rate setting of project boiler i |  | 3.3 | % | Blow flow rate setting specified in the boiler water treatment program for a water purification/demineralization system such as RO based on the test result
| BFRE | Blow flow rate setting of reference boiler |  | 9.2 | % | Blow flow rate specified in the boiler water treatment program for a water softener based on the test result
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 196 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)
Monitoring Spreadsheet: JCM_ID_AM015_ver01.0
Reference Number: ID022
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  | N/A | 196.6628 | tCO2/p | ERp
2. Selected default values, etc.
| Efficiency of project boiler i |  |  | N/A | 0.95 | - | ηi,PJ
| Efficiency of reference boiler |  |  | N/A | 0.89 | - | ηRE
| Blow flow rate setting of project boiler |  |  | N/A | 3.3 | % | BFi,PJ
| Blow flow rate setting of reference boiler |  |  | N/A | 9.2 | % | BFRE
3. Calculations for reference emissions
| Reference emissions during the period p |  |  | N/A | 1634.5268 | tCO2/p | REp
|  | Fuel consumption of project boiler i using the fuel type j during the period p (for natural gas or LPG) |  | Natural gas/LPG | 800000 | Nm3/p or t/p | FCp,i,j,PJ
|  | Fuel consumption of project boiler i using the fuel type j during the period p (for diesel oil) |  | Diesel | 0 | t/p | FCp,i,j,PJ
|  | Net calorific value of fuel used by the project boiler i for the fuel type j (for natural gas or LPG) |  | Natural gas/LPG | 0.0331 | GJ/Nm3 or GJ/t | NCVi,j,PJ
|  | Net calorific value of fuel used by the project boiler i for the fuel type j (for diesel oil) |  | Diesel | 0 | GJ/t | NCVi,j,PJ
|  | CO2 emission factor of fuel used by the reference boiler |  | Natural gas/LPG /Diesel/Coal | 0.0543 | tCO2/GJ | EFRE
|  | Efficiency of project boiler i |  | N/A | 0.95 | - | ηi,PJ
|  | Efficiency of reference boiler |  | N/A | 0.89 | - | ηRE
|  | Blow flow rate setting of project boiler i |  | N/A | 3.3 | % | BFi,PJ
|  | Blow flow rate setting of reference boiler |  | N/A | 9.2 | % | BFRE
4. Calculations of the project emissions
| Project emissions during the period p |  |  | N/A | 1437.864 | tCO2/p | PEp
|  | Fuel consumption of project boiler i using the fuel type j during the period p (for natural gas or LPG) |  | Natural gas/LPG | 800000 | Nm3/p or t/p | FCp,i,j,PJ
|  | Fuel consumption of project boiler i using the fuel type j during the period p (for diesel oil) |  | Diesel | 0 | t/p | FCp,i,j,PJ
|  | Net calorific value of fuel used by the project boiler i for the fuel type j (for natural gas or LPG) |  | Natural gas/LPG | 0.0331 | GJ/Nm3 or GJ/t | NCVi,j,PJ
|  | Net calorific value of fuel used by the project boiler i for the fuel type j (for diesel oil) |  | Diesel | 0 | GJ/t | NCVi,j,PJ
|  | CO2 emission factor of fuel used by the project boiler i for the fuel type j (for natural gas or LPG) |  | Natural gas/LPG | 0.0543 | tCO2/GJ | EFi,j,PJ
|  | CO2 emission factor of fuel used by the project boiler i for the fuel type j (for diesel oil) |  | Diesel | 0 | tCO2/GJ | EFi,j,PJ
[List of Default Values]
|  |  | Net calorific value of natural gas | 0.0331 | GJ/Nm3
|  |  | Net calorific value of LPG | 44.8 | GJ/t
|  |  | Net calorific value of diesel | 41.4 | GJ/t
|  |  |  | EFRE (Lower) | EFi,j,PJ (Default)
|  |  | CO2 emission factor of natural gas | 0.0543 | 0.0561 | tCO2/GJ
|  |  | CO2 emission factor of LPG | 0.0616 | 0.0631 | tCO2/GJ
|  |  | CO2 emission factor of diesel | 0.0726 | 0.0741 | tCO2/GJ
|  |  | CO2 emission factor of kerosene | 0.0708 | 0.0719 | tCO2/GJ
|  |  | CO2 emission factor of HFO | 0.0755 | 0.0774 | tCO2/GJ
|  |  | CO2 emission factor of Coal | 0.0909 | 0.101 | tCO2/GJ

## MSS
Monitoring Spreadsheet: JCM_ID_AM015_ver01.0
Reference Number: ID022
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| General manager | To approve the monitoring results and submit monitoring reports to Sumitomo Rubber Industry. To keep and archive monitored and required data in the verification and issuance for two years after the final issuance of credits
| Assistant manager | To check operational situation of the chiller, compile monitoring data and create monitoring report.

## MRS(input)
Monitoring Spreadsheet: JCM_ID_AM015_ver01.0
Reference Number: ID022
Monitoring Report Sheet (Input Sheet) [For Verification]
Table 1: Parameters monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k)
| Monitoring period | Monitoring point No. | Parameters | Description of data | Monitored Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
|  | (1) | FCp,i,j,PJ | The amount of fuel consumption of project boiler i using the fuel type j (=natural gas or LPG) during the period p |  | Nm3/p or t/p | Option B or Option C | Invoice from fuel supply company or measured data | [For Option B] Data is collected and recorded from the invoices by the fuel supply company. [For Option C] Data is measured by measuring equipments in the factory. - Specification of measuring equipments: 1) Fuel flow meter is applied for measurement of fuel consumption of the project boilers. 2) Meter is certified in compliance with national / regional / international standards on fuel flow meter. - Measuring and recording: 1) Measured data is automatically sent to a server where data is recorded and stored. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of installation. | Continuously | For natural gas or LPG
|  | (2) | FCp,i,j,PJ | The amount of fuel consumption of project boiler i using the fuel type j (=diesel oil) during the period p |  | t/p | Option B or Option C | Invoice from fuel supply company or measured data | [For Option B] Data is collected and recorded from the invoices by the fuel supply company. [For Option C] Data is measured by measuring equipments in the factory. - Specification of measuring equipments: 1) Fuel flow meter is applied for measurement of fuel consumption of the project boilers. 2) Meter is certified in compliance with national / regional / international standards on fuel flow meter. - Measuring and recording: 1) Measured data is automatically sent to a server where data is recorded and stored. 2) Recorded data is checked its integrity once a month by responsible staff. - Calibration: The measuring instrument(s) is replaced or calibrated at an interval following the regulations in the country in which the measuring instrument(s) is commonly used or according to the manufacturer’s recommendation, unless a type approval, manufacturer’s specification, or certification issued by an entity accredited under international/national standards for the measuring instrument(s) has been prepared by the time of installation. | Continuously | For diesel oil
Table 2: Project-specific parameters fixed ex ante
| (a) |  | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters |  | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| NCVi,j,PJ |  | Net calorific value of fuel used by the project boiler i for the fuel type j |  | 0.0331 | GJ/Nm3 or GJ/t | (1) Net calorific value (lower heating value) provided by fuel supplier or boiler manufacturer, (2) IPCC default values at the lower limit in Table 1.2 of Chapter 1 of Vol. 2 of the “2006 IPCC Guidelines on National GHG Inventories” (when (1) is not available, apply (2)) |  |  | For natural gas or LPG
| NCVi,j,PJ |  | Net calorific value of fuel used by the project boiler i for the fuel type j |  | 0 | GJ/t | (1) Net calorific value (lower heating value) provided by fuel supplier or boiler manufacturer, (2) IPCC default values at the lower limit in Table 1.2 of Chapter 1 of Vol. 2 of the “2006 IPCC Guidelines on National GHG Inventories” (when (1) is not available, apply (2)) |  |  | For diesel oil
| EFi,j,PJ |  | CO2 emission factor of fuel used by the project boiler i for the fuel type j |  | 0.0543 | tCO2/GJ | IPCC default values in Table 1.4 of Chapter 1 of Vol. 2 of the “2006 IPCC Guidelines on National GHG Inventories" |  |  | For natural gas or LPG
| EFi,j,PJ |  | CO2 emission factor of fuel used by the project boiler i for the fuel type j |  | 0 | tCO2/GJ | IPCC default values in Table 1.4 of Chapter 1 of Vol. 2 of the “2006 IPCC Guidelines on National GHG Inventories" |  |  | For diesel oil
| EFRE |  | CO2 emission factor of fuel used by reference boiler |  | 0.0543 | tCO2/GJ | IPCC default values at the lower limit in Table 1.4 of Chapter 1 of Vol. 2 of the “2006 IPCC Guidelines on National GHG Inventories" In case the project boiler replaces the existing boiler or the planned boiler whose plan is once approved officially such as with boiler installation permit or environmental impact assessment, CO2 emission factor of the fuel used by the existing or planned boiler is applied. Otherwise, the value of the fuel used by the project boiler i is applied.
| ηi,PJ |  | Efficiency of project boiler i |  | 0.95 | - | Specifications of the project boiler or factory test data of the project boiler by the manufacturer
| ηRE |  | Efficiency of reference boiler |  | 0.89 | - | The default value set in the methodologies
| BFi,PJ |  | Blow flow rate setting of project boiler i |  | 3.3 | % | Blow flow rate setting specified in the boiler water treatment program for a water purification/demineralization system such as RO based on the test result
| BFRE |  | Blow flow rate setting of reference boiler |  | 9.2 | % | Blow flow rate specified in the boiler water treatment program for a water softener based on the test result
Table3: Ex-post calculation of CO2 emission reductions
| Monitoring Period | CO2 emission reductions |  | Units
|  | 0 |  | tCO2/p
[Monitoring option]
| Option A |  | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B |  | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C |  | Based on the actual measurement using measuring equipments (Data used: measured values)

## MRS(calc_process)
Monitoring Spreadsheet: JCM_ID_AM015_ver01.0
Reference Number: ID022
Monitoring Report Sheet (Calculation Process Sheet) [For Verification]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  | N/A | 0 | tCO2/p | ERp
2. Selected default values, etc.
| Efficiency of project boiler i |  |  | N/A | 0.95 | - | ηi,PJ
| Efficiency of reference boiler |  |  | N/A | 0.89 | - | ηRE
| Blow flow rate setting of project boiler |  |  | N/A | 3.3 | % | BFi,PJ
| Blow flow rate setting of reference boiler |  |  | N/A | 9.2 | % | BFRE
3. Calculations for reference emissions
| Reference emissions during the period p |  |  | N/A | 0 | tCO2/p | REp
|  | Fuel consumption of project boiler i using the fuel type j during the period p (for natural gas or LPG) |  | Natural gas/LPG | 0 | Nm3/p or t/p | FCp,i,j,PJ
|  | Fuel consumption of project boiler i using the fuel type j during the period p (for diesel oil) |  | Diesel | 0 | t/p | FCp,i,j,PJ
|  | Net calorific value of fuel used by the project boiler i for the fuel type j (for natural gas or LPG) |  | Natural gas/LPG | 0.0331 | GJ/Nm3 or GJ/t | NCVi,j,PJ
|  | Net calorific value of fuel used by the project boiler i for the fuel type j (for diesel oil) |  | Diesel | 0 | GJ/t | NCVi,j,PJ
|  | CO2 emission factor of fuel used by the reference boiler |  | Natural gas/LPG /Diesel/Coal | 0.0543 | tCO2/GJ | EFRE
|  | Efficiency of project boiler i |  | N/A | 0.95 | - | ηi,PJ
|  | Efficiency of reference boiler |  | N/A | 0.89 | - | ηRE
|  | Blow flow rate setting of project boiler i |  | N/A | 3.3 | % | BFi,PJ
|  | Blow flow rate setting of reference boiler |  | N/A | 9.2 | % | BFRE
4. Calculations of the project emissions
| Project emissions during the period p |  |  | N/A | 0 | tCO2/p | PEp
|  | Fuel consumption of project boiler i using the fuel type j during the period p (for natural gas or LPG) |  | Natural gas/LPG | 0 | Nm3/p or t/p | FCp,i,j,PJ
|  | Fuel consumption of project boiler i using the fuel type j during the period p (for diesel oil) |  | Diesel | 0 | t/p | FCp,i,j,PJ
|  | Net calorific value of fuel used by the project boiler i for the fuel type j (for natural gas or LPG) |  | Natural gas/LPG | 0.0331 | GJ/Nm3 or GJ/t | NCVi,j,PJ
|  | Net calorific value of fuel used by the project boiler i for the fuel type j (for diesel oil) |  | Diesel | 0 | GJ/t | NCVi,j,PJ
|  | CO2 emission factor of fuel used by the project boiler i for the fuel type j (for natural gas or LPG) |  | Natural gas/LPG | 0.0543 | tCO2/GJ | EFi,j,PJ
|  | CO2 emission factor of fuel used by the project boiler i for the fuel type j (for diesel oil) |  | Diesel | 0 | tCO2/GJ | EFi,j,PJ
[List of Default Values]
|  |  | Net calorific value of natural gas | 0.0331 | GJ/Nm3
|  |  | Net calorific value of LPG | 44.8 | GJ/t
|  |  | Net calorific value of diesel | 41.4 | GJ/t
|  |  |  | EFRE (Lower) | EFi,j,PJ (Default)
|  |  | CO2 emission factor of natural gas | 0.0543 | 0.0561 | tCO2/GJ
|  |  | CO2 emission factor of LPG | 0.0616 | 0.0631 | tCO2/GJ
|  |  | CO2 emission factor of diesel | 0.0726 | 0.0741 | tCO2/GJ
|  |  | CO2 emission factor of kerosene | 0.0708 | 0.0719 | tCO2/GJ
|  |  | CO2 emission factor of HFO | 0.0755 | 0.0774 | tCO2/GJ
|  |  | CO2 emission factor of Coal | 0.0909 | 0.101 | tCO2/GJ