## MPS(input)
Monitoring Spreadsheet: JCM_ID_AM010_ver01.0
Sectoral scope: 03
Monitoring Plan Sheet (Input Sheet) [Attachment to Project Design Document]
Table 1: Parameters to be monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j)
| Monitoring point No. | Parameters | Description of data | Estimated Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
| (1) | QPJh,p | Quantity of heating energy utilized by the project building during the period p | 3784 | GJ/p | Option C | monitored data | Quantity of heating energy utilized by the project building is determined either by (1) a calorimeter or (2) calculation results using a set of different monitored data. In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 such as SNI-19-17025-2006 is not provided, such monitoring equipment is required to be calibrated. [Approach 1 using a calorimeter] The calorimeter measures the heating value cumulatively for each equipment. [Approach 2 applying calculation results of monitored data] Following formula from the methodology is applied: Where, mPJh,i,t :Quantity of hot water utilized by the equipment i in the project building between time t-1 and time t Th-0,i,t : Outlet temperature of the hot water at time t Th-1,i,t :Inlet temperature of the feed water for hot water at time t mPJh,i,t is measured with a flow meter while Th-0,i,t and Th-1,i,t are measured with thermometers. | [Approach 2] Monitored at least hourly basis and recorded daily | Approach 2 is selected
| (2) | QPJc,p | Quantity of cooling energy utilized by the project building during the period p | 3405 | GJ/p | Option C | monitored data | Quantity of cooling energy utilized by the project building is determined either by (1) a calorimeter or (2) calculation results using a set of different monitored data. 'In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 such as SNI-19-17025-2006 is not provided, such monitoring equipment is required to calibrate. [Approach 1 using a calorimeter] The calorimeter measures the heating value cumulatively for each equipment. [Approach 2 applying calculation results of monitored data] Following formula from the methodology is applied: Where, mPJc,i,t :Quantity of chilled water utilized by the equipment i in the project building between time t-1 and time t Th-0,i,t : Inlet temperature of the feed water for chilled water at time t Th-1,i,t : Outlet temperature of the chilled water at time t mPJc,i,t is measured with a flow meter while Th-0,i,t and Th-1,i,t are measured with thermometers. | [Approach 2] Monitored at least hourly basis and recorded daily | Approach 2 is selected
| (3) | FCPJ,p | Oil consumed by the project during the period p | 0 | kL/p | Option B or Option C | Invoice from fuel supplier for Option B or monitored data for Option C | [Option B] Recorded from invoices provided by the fuel supplier. [Option C] Measured with a flow meter, calibrated according to the national regulation. In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 such as SNI-19-17025-2006 is not provided, such monitoring equipment is required to calibrate. | Recorded Monthly | Neither heat pump nor auxiliary equipment installed by the project consumes fossil fuel
| (4) | ECHP,m,p | Electricity consumed by the modular HP m operated during the period p | 374 | MWh/p | Option C | monitored data | 'Measured with an electric meter. In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 such as SNI-19-17025-2006 is not provided, such monitoring equipment is required to calibrate. Data are recorded at least once a month. | Monitored continuously and recorded monthly
| (5) | ECHP_aux,m,p | Electricity consumed by auxiliary electric equipment for the modular HP m operated during the period p | 36 | MWh/p | Option C | monitored data | Measured with an electric meter. In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 such as SNI-19-17025-2006 is not provided, such monitoring equipment is required to calibrate. Data are recorded at least once a month. | Monitored continuously and recorded monthly
| (6) | ECOther,n,p | Electricity consumed by other chilled water generating equipment n operated during the period p | 0 | MWh/p | Option C | monitored data | Measured with an electric meter. In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 such as SNI-19-17025-2006 is not provided, such monitoring equipment is required to calibrate. Data are recorded at least once a month. | Monitored continuously and recorded monthly
| (7) | ECOther_aux,n,p | Electricity consumed by auxiliary electric equipment for the other chilled water generating equipment n during the period p | 0 | MWh/p | Option C | monitored data | Measured with an electric meter. In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 such as SNI-19-17025-2006 is not provided, such monitoring equipment is required to calibrate. Data are recorded at least once a month. | Monitored continuously and recorded monthly
Table 2: Project-specific parameters to be fixed ex ante
| (a) | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| ηREh | Efficiency of the reference equipment for heating energy generation |  | 0.9 | dimensionless | Default value in the methodology (from the CDM methodological tool "Tool to determine the baseline efficiency of thermal or electric energy generation systems", ver.01).
| ηREc | Efficiency of the reference equipment for cooling energy generation |  | 3.7 | dimensionless | Default value in the methodology (from the latest National Standard of Indonesia SNI 6390 available at the time of validation).
| EFREh | CO2 emission factor for the oil consumed by the reference equipment for heating energy generation |  | 0.0726 | tCO2/GJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
| Cp | Specific heat capacity of water |  | 4.186 | MJ/tonne- degree Celsius
| ρ | Density of water |  | 1 | tonne/m3
| EFelec | CO2 emission factor for the electricity consumed by the project and the reference equipment When the project equipment consumes only grid electricity or captive electricity, the project participant applies the CO2 emission factor respectively. When the project equipment may consume both grid electricity and captive electricity, the project participant applies the CO2 emission factor with lower value. [CO2 emission factor] For grid electricity: The most recent value available from the source stated in this table at the time of validation For captive electricity: 0.8* [tCO2/MWh] *The most recent value available from CDM approved small scale methodology AMS-I.A at the time of validation is applied. |  | 0.84 | tCO2/MWh | [EFgrid] The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism (Indonesian DNA for CDM), based on data obtained by Directorate General of Electricity, Ministry of Energy and Mineral Resources, Indonesia, unless otherwise instructed by the Joint Committee. [EFcaptive] CDM approved small scale methodology AMS-I.A
| EFfuel | CO2 emission factor for the oil consumed by the project |  |  | tCO2/kL | In the order of preference: a) values provided by the fuel supplier; b) measurement by the project participants; c) regional or national default values; d) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | No fossil fuel consumption within the project boundary is anticipated.
Table3: Ex-ante estimation of CO2 emission reductions
| CO2 emission reductions |  | Units
| 175 |  | tCO2/p
[Monitoring option]
| Option A | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C | Based on the actual measurement using measuring equipments (Data used: measured values)

## MPS(calc_process)
Monitoring Spreadsheet: JCM_ID_AM010_ver01.0
Sectoral scope: 03
Monitoring Plan Sheet (Calculation Process Sheet) [Attachment to Project Design Document]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  | N/A | 175 | tCO2/p | ERp
2. Selected default values, etc.
| Efficiency of the reference equipment for heating energy generation |  |  | N/A | 0.9 | - | ηREh
| Efficiency of the reference equipment for cooling energy generation |  |  | N/A | 3.7 | - | ηREc
3. Calculations for reference emissions
| Reference emissions during the period p |  |  | N/A | 519.9724 | tCO2/p | REp
|  | Quantity of heating energy utilized by the project building during the period p |  | N/A | 3784 | GJ/y | QPJh,p
|  | Quantity of cooling energy utilized by the project building during the period p |  | N/A | 3405 | GJ/y | QPJc,p
|  | Efficiency of the reference equipment for heating energy generation |  | N/A | 0.9 | -- | ηREh
|  | Efficiency of the reference equipment for cooling energy generation |  | N/A | 3.7 | -- | ηREc
|  | CO2 emission factor for the oil consumed by the reference equipment for heating energy generation |  | Oil | 0.0726 | tCO2/GJ | EFREh
|  | CO2 emission factor for the electricity consumed by the project |  | Electricity | 0.84 | tCO2/MWh | EFelec
4. Calculations of the project emissions
| Project emissions during the period p |  |  | N/A | 344.4 | tCO2/p | PEp
|  | Electricity consumed by the project during the period p |  | Electricity | 410 | MWh/p | ECPJ,p
|  | CO2 emission factor for the electricity consumed by the project |  | N/A | 0.84 | tCO2/MWh | EFelec
|  | Oil consumed by the project during the period p |  | Oil | 0 | kL/p | FCPJ,p
|  | CO2 emission factor for the oil consumed by the project |  | N/A | 0 | tCO2/kL | EFfuel
|  | Electricity consumed by the modular HP m operated during the period p |  | Electricity | 374 | MWh/p | ECHP,m,p
|  | Electricity consumed by auxiliary electric equipment for the modular HP m during the period p |  | Electricity | 36 | MWh/p | ECHP_aux,m,p
|  | Electricity consumed by other chilled water generating equipment n operated during the period p |  | Electricity | 0 | MWh/p | ECOther,n,p
|  | Electricity consumed by auxiliary electric equipment for the other chilled water generating equipment n during the period p |  | Electricity | 0 | MWh/p | ECother_aux,n,p
[List of Default Values]
|  |  | Efficiency of the reference equipment for heating energy generation | 0.9 | - | ηREh
|  |  | Efficiency of the reference equipment for cooling energy generation | 3.7 | - | ηREc
|  |  | Specific heat capacity of water | 4.186 | - | Cp
|  |  | Density of water | 1 | - | ρ

## MSS
Monitoring Spreadsheet: JCM_ID_AM010_ver01.0
Sectoral scope: 03
Monitoring Structure Sheet [Attachment to Project Design Document]
| Responsible personnel | Role
| Project Manager | Responsible for project implementation, monitoring results and reporting for JCM procedure
| Monitoring Manager | In charge of confirming the recorded data and archived data.
| Facility Manager | In charge of operation and maintenance of the project facilities
| Operator | In charge of collecting and archiving the data

## MRS(input)
Monitoring Spreadsheet: JCM_ID_AM010_ver01.0
Sectoral scope: 03
Monitoring Report Sheet (Input Sheet) [For Verification]
Table 1: Parameters monitored ex post
| (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h) | (i) | (j) | (k)
| Monitoring period | Monitoring point No. | Parameters | Description of data | Monitored Values | Units | Monitoring option | Source of data | Measurement methods and procedures | Monitoring frequency | Other comments
|  | (1) | QPJh,p | Quantity of heating energy utilized by the project building during the period p |  | GJ/p | Option C | monitored data | Quantity of heating energy utilized by the project building is determined either by (1) a calorimeter or (2) calculation results using a set of different monitored data. In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 such as SNI-19-17025-2006 is not provided, such monitoring equipment is required to be calibrated. [Approach 1 using a calorimeter] The calorimeter measures the heating value cumulatively for each equipment. [Approach 2 applying calculation results of monitored data] Following formula from the methodology is applied: Where, mPJh,i,t :Quantity of hot water utilized by the equipment i in the project building between time t-1 and time t Th-0,i,t : Outlet temperature of the hot water at time t Th-1,i,t :Inlet temperature of the feed water for hot water at time t mPJh,i,t is measured with a flow meter while Th-0,i,t and Th-1,i,t are measured with thermometers. | [Approach 1] Monitored continuously and recorded at least monthly [Approach 2] Monitored at t interval (at least hourly basis) and recorded at least daily
|  | (2) | QPJc,p | Quantity of cooling energy utilized by the project building during the period p |  | GJ/p | Option C | monitored data | Quantity of cooling energy utilized by the project building is determined either by (1) a calorimeter or (2) calculation results using a set of different monitored data. 'In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 such as SNI-19-17025-2006 is not provided, such monitoring equipment is required to calibrate. [Approach 1 using a calorimeter] The calorimeter measures the heating value cumulatively for each equipment. [Approach 2 applying calculation results of monitored data] Following formula from the methodology is applied: Where, mPJc,i,t :Quantity of chilled water utilized by the equipment i in the project building between time t-1 and time t Th-0,i,t : Inlet temperature of the feed water for chilled water at time t Th-1,i,t : Outlet temperature of the chilled water at time t mPJc,i,t is measured with a flow meter while Th-0,i,t and Th-1,i,t are measured with thermometers. | [Approach 1] Monitored continuously and recorded at least monthly [Approach 2] Monitored at t interval (at least hourly basis) and recorded at least daily
|  | (3) | FCPJ,p | Oil consumed by the project during the period p |  | kL/p | Option B or Option C | Invoice from fuel supplier for Option B or monitored data for Option C | [Option B] Recorded from invoices provided by the fuel supplier. [Option C] Measured with a flow meter, calibrated according to the national regulation. In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 such as SNI-19-17025-2006 is not provided, such monitoring equipment is required to calibrate. | Recorded Monthly
|  | (4) | ECHP,m,p | Electricity consumed by the modular HP m operated during the period p |  | MWh/p | Option C | monitored data | 'Measured with an electric meter. In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 such as SNI-19-17025-2006 is not provided, such monitoring equipment is required to calibrate. Data are recorded at least once a month. | Monitored continuously and recorded monthly
|  | (5) | ECHP_aux,m,p | Electricity consumed by auxiliary electric equipment for the modular HP m operated during the period p |  | MWh/p | Option C | monitored data | Measured with an electric meter. In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 such as SNI-19-17025-2006 is not provided, such monitoring equipment is required to calibrate. Data are recorded at least once a month. | Monitored continuously and recorded monthly
|  | (6) | ECOther,n,p | Electricity consumed by other chilled water generating equipment n operated during the period p |  | MWh/p | Option C | monitored data | Measured with an electric meter. In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 such as SNI-19-17025-2006 is not provided, such monitoring equipment is required to calibrate. Data are recorded at least once a month. | Monitored continuously and recorded monthly
|  | (7) | ECOther_aux,n,p | Electricity consumed by auxiliary electric equipment for the other chilled water generating equipment n during the period p |  | MWh/p | Option C | monitored data | Measured with an electric meter. In case a calibration certificate issued by an entity accredited under ISO/IEC 17025 or any other accreditation standards conforming to ISO/IEC 17025 such as SNI-19-17025-2006 is not provided, such monitoring equipment is required to calibrate. Data are recorded at least once a month. | Monitored continuously and recorded monthly
Table 2: Project-specific parameters fixed ex ante
| (a) |  | (b) |  | (c) | (d) | (e) |  |  | (f)
| Parameters |  | Description of data |  | Estimated Values | Units | Source of data |  |  | Other comments
| ηREh |  | Efficiency of the reference equipment for heating energy generation |  | 0.9 | dimensionless | Default value in the methodology (from the CDM methodological tool "Tool to determine the baseline efficiency of thermal or electric energy generation systems", ver.01).
| ηREc |  | Efficiency of the reference equipment for cooling energy generation |  | 3.7 | dimensionless | Default value in the methodology (from the latest National Standard of Indonesia SNI 6390 available at the time of validation).
| EFREh |  | CO2 emission factor for the oil consumed by the reference equipment for heating energy generation |  | 0.0726 | tCO2/GJ | IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied.
| Cp |  | Specific heat capacity of water |  | 4.186 | MJ/tonne- degree Celsius
| ρ |  | Density of water |  | 1 | tonne/m3
| EFelec |  | CO2 emission factor for the electricity consumed by the project and the reference equipment When the project equipment consumes only grid electricity or captive electricity, the project participant applies the CO2 emission factor respectively. When the project equipment may consume both grid electricity and captive electricity, the project participant applies the CO2 emission factor with lower value. [CO2 emission factor] For grid electricity: The most recent value available from the source stated in this table at the time of validation For captive electricity: 0.8* [tCO2/MWh] *The most recent value available from CDM approved small scale methodology AMS-I.A at the time of validation is applied. |  | 0.84 | tCO2/MWh | [EFgrid] The data is sourced from “Emission Factors of Electricity Interconnection Systems”, National Committee on Clean Development Mechanism (Indonesian DNA for CDM), based on data obtained by Directorate General of Electricity, Ministry of Energy and Mineral Resources, Indonesia, unless otherwise instructed by the Joint Committee. [EFcaptive] CDM approved small scale methodology AMS-I.A
| EFfuel |  | CO2 emission factor for the oil consumed by the project |  | 0 | tCO2/kL | In the order of preference: a) values provided by the fuel supplier; b) measurement by the project participants; c) regional or national default values; d) IPCC default values provided in table 1.4 of Ch.1 Vol.2 of 2006 IPCC Guidelines on National GHG Inventories. Lower value is applied. |  |  | No fossil fuel consumption within the project boundary is anticipated.
Table3: Ex-post calculation of CO2 emission reductions
| Monitoring Period |  | CO2 emission reductions |  | Units
|  |  | 0 |  | tCO2/p
[Monitoring option]
| Option A |  | Based on public data which is measured by entities other than the project participants (Data used: publicly recognized data such as statistical data and specifications)
| Option B |  | Based on the amount of transaction which is measured directly using measuring equipments (Data used: commercial evidence such as invoices)
| Option C |  | Based on the actual measurement using measuring equipments (Data used: measured values)

## MRS(calc_process)
Monitoring Spreadsheet: JCM_ID_AM010_ver01.0
Sectoral scope: 03
Monitoring Report Sheet (Calculation Process Sheet) [For Verification]
1. Calculations for emission reductions |  |  |  | Fuel type | Value | Units | Parameter
| Emission reductions during the period p |  |  | N/A | 0 | tCO2/p | ERp
2. Selected default values, etc.
| Efficiency of the reference equipment for heating energy generation |  |  | N/A | 0.9 | - | ηREh
| Efficiency of the reference equipment for cooling energy generation |  |  | N/A | 3.7 | - | ηREc
3. Calculations for reference emissions
| Reference emissions during the period p |  |  | N/A | 0 | tCO2/p | REp
|  | Quantity of heating energy utilized by the project building during the period p |  | N/A | 0 | GJ/y | QPJh,p
|  | Quantity of cooling energy utilized by the project building during the period p |  | N/A | 0 | GJ/y | QPJc,p
|  | Efficiency of the reference equipment for heating energy generation |  | N/A | 0.9 | -- | ηREh
|  | Efficiency of the reference equipment for cooling energy generation |  | N/A | 3.7 | -- | ηREc
|  | CO2 emission factor for the oil consumed by the reference equipment for heating energy generation |  | Oil | 0.0726 | tCO2/GJ | EFREh
|  | CO2 emission factor for the electricity consumed by the project |  | Electricity | 0.84 | tCO2/MWh | EFelec
4. Calculations of the project emissions
| Project emissions during the period p |  |  | N/A | 0 | tCO2/p | PEp
|  | Electricity consumed by the project during the period p |  | Electricity | 0 | MWh/p | ECPJ,p
|  | CO2 emission factor for the electricity consumed by the project |  | N/A | 0.84 | tCO2/MWh | EFelec
|  | Oil consumed by the project during the period p |  | Oil | 0 | kL/p | FCPJ,p
|  | CO2 emission factor for the oil consumed by the project |  | N/A | 0 | tCO2/kL | EFfuel
|  | Electricity consumed by the modular HP m operated during the period p |  | Electricity | 0 | MWh/p | ECHP,m,p
|  | Electricity consumed by auxiliary electric equipment for the modular HP m during the period p |  | Electricity | 0 | MWh/p | ECHP_aux,m,p
|  | Electricity consumed by other chilled water generating equipment n operated during the period p |  | Electricity | 0 | MWh/p | ECOther,n,p
|  | Electricity consumed by auxiliary electric equipment for the other chilled water generating equipment n during the period p |  | Electricity | 0 | MWh/p | ECother_aux,n,p
[List of Default Values]
|  |  | Efficiency of the reference equipment for heating energy generation | 0.9 | - | ηREh
|  |  | Efficiency of the reference equipment for cooling energy generation | 3.7 | - | ηREc
|  |  | Specific heat capacity of water | 4.186 | - | Cp
|  |  | Density of water | 1 | - | ρ